ISOR 160 E2 20 – ID 135005

Sound proof tube fan in steel casing

Fully insulated fan box for mounting in ventilation tubes. For easy mounting in tubes, the connecting pieces are provided with a lip seal. Housing made of galvanized sheet steel with sound-absorbing inner lining of 40 mm mineral wool with abrasion resistant glass fiber coating according to DIN EN 13 501-1 Class A1. Mounting position horizontally and vertically possible. Through a removable cap, the swing-out fan unit is easy to clean. Ventilator unit easily removable from the sound proof casing. With integrated mounting bracket for easy installation.

An efficiency-optimized impeller with backward curved blades is fitted on the external rotor of a voltage controllable motor. The impeller is balanced according to the quality class G 6.3 of DIN / ISO 1940, on 2 planes. Closed drive motor, maintenance-free ball bearings with lifetime lubrication, sealed on both sides. All fans with standard motor protection using thermal contact and internally connected motor capacitor. The electrical connection is to be done via an external terminal box IP44.

CE marking according to EC Declaration of Conformity for Electromagnetic Compatibility EMC - Directive 2004/108/EC. EC - Declaration of Incorporation according to the Machinery Directive 2006/42/EC - Directive 2009/125/EC (Reg. 1253/2014/EU).

Technical Data

Volumetric flow (V):

m³/h

Pressure increase (pfa):

Pa

SFP Wert

W/(m3/s)

Voltage (U):

1~230 V

Frequency (f):

50 Hz

Power consumption max. (P1):

49 W

Current consumption max. (I):

0,3 A

Rated speed (n):

2390 min-1

Capacitor:

2 µF

Protection class terminal box:

IP44

Inlet sound power level (LWA5):

53 dB(A)

Outlet sound power level (LWA6):

66 dB(A)

Casing sound power level (LWA2):

50 dB(A)

Max. medium temperature (t):

70°C

Dimensions (L x W x H):

378 x 380 x 232 mm

Connection diameter:

160

Weight:

11,8 kg

Wiring diagram:

116985

Manufacturer:

ruck Ventilatoren GmbH

Max-Planck-Str. 5

97944 Boxberg

Tel. 07930-9211300

www.ruck.eu

Type:

ISOR 160 E2 20

Item number:

135005

Available accessories:

VM 160		102649		Fast clamps, 1 Set = 2 Pieces, size 160

RSK 160 D	113485	 	Backdraught shutter with seal size 160

RSK 160		102661	 	Backdraught shutter size 160

SDS 160		102717	 	Silencer rigid, 1m, sound insulation 50mm, size 160

SDF 160		102703	 	Silencer flexible, 1m, sound insulation 50mm, size 160

FT 160		112841 		Filter box for pocket filter (without pocket filter) size 160

LFT 05 F5	102939		Pocket filter, M5, size 1, for FT 100-250

LFT 05 F7	102945		Pocket filter, F7, size 1, for FT 100-250

FTW 160		112852	 	Filter box with integrated heating coil, M5 Pocket filter, size 160

FV 160		112831		Filter box with mat filter, size 160

SG 160 01	102897		Protection grille size 160

RD ISOR 01	129882		Rain cover ISOR 01

GS 01		102787		Isolator switch (loose)

MTY 1		103428		Electronic controller, stepless

TEE 015		115893		5-step transformer without motor protection (surface mounting)

TES 0145	111858		7-step transformer without protection for switch cabinet